TERMS OF REFERENCE

BIDDING FOR THE SUPPLY, DELIVERY, INSTALLATION, TESTING AND COMMISSIONING OF ONE (1) UNIT 600KVA GENERATOR SET WITH AUTOMATIC TRANSFER SWITCH (ATS) FOR TMO-MASAO, PHILIPPINE PORTS AUTHORITY

- OBJECTIVE:

To provide generator set for TMO-Masao to ensure the continuous supply of power during brown-outs/power outrage from local power service provider.

- SCOPE OF WORK:

The work to be executed and completed and equipment to be deployed by the Supplier at TMO-Masao as identified by the PPA shall include the following:

- Mobilization of manpower, materials, tools, equipment and technical supervisions.

- Construction of Concrete Pedestal and shed.

- Supply, delivery, installation, testing and commissioning of brand new generator set and all ancillary equipment required for installation and operation.

- Supply and installation of Cable wires and panel board from generator set to 1600 Ampere Automatic Transfer Switch (ATS) and Main Distribution Panel.

- Installation of appropriate safety measures at the project site.

- Provision of warranties:

  - Two (2) years warranty against manufacturer’s defects from receipt of the Certificate of Acceptance.

  - Three (3) years warranty for parts and services from the date of receipt of the Certificate of Acceptance.

- Actual Load Testing before final acceptance.

- Conduct of one (1) day training for the end-user operator on operating system, commissioning and preventive maintenance procedure.

- Supplier/Contractor must at least be ten (10) years in the market of supplying generator set.

- Supplier/Contractor must have a professional Electrical Engineer employed with valid PRC License and Professional Tax Receipt.

- Supplier/Contractor must have a professional Mechanical Engineer employed with valid PRC License and Professional Tax Receipt.

- Supplier/Contractor must have a service center in Region XIII-Caraga to accommodate the after –sales services (quick response).

- Generator set is a soundproof/weather proof (imported enclosure) from the manufacturer.

- Supplier/Contractor must provide/secure “Permit to Operate” for Air Pollution Source and Control Installation of Generator Set from Environmental Management Bureau (EMB).

- Red Ribbon Certification from the Supplier.

- MATERIAL SPECIFICATION:

| 600 kVA GENERATOR SET SPECIFICATION |
| --- |
| Number of cylinders | Six (6) |
| Cylinder arrangement | In-line |
| Aspiration | Turbocharged after-water cooling |
| Prime Rating Power (kW/kVA) | 432kW/540kVA |
| Standby Rating Power (kW/kVA) | 480kW/600kVA |
| Control Panel | Digital |
| Speed governor | Electrical |
| Cooling System | Water Cooling Cycle |
| Phase | Three (3) |
| Rpm | 1800 |
| Volts | 230Vac |
| Frequency | 60Hz |
| Power Factor | 0.8 |
| Fuel consumption at 100% load (L/H) | 111 |
| Insulation | Clash H |
| Starter Motor | 24V |
| Exciter type | Single bearing, brushless, self-excited |

1600 AMPERE AUTOMATIC TRANSFER SWITCH SPECIFICATION

Ratings 40 to 3000 Amps (3 poles)

UL 1008 listed at 480 VAC

Double throw, mechanically interlocked contractor mechanism

Electrically operated, mechanically held

Designed for emergency and standby applications

Timer and voltage/frequency settings adjustable without disconnection from the power section

Built-in diagnostic with an LCD display for immediate troubleshooting

LED/LCD indicators for ease of viewing and long life

Nonvolatile memory-clock battery back-up not required for standard switch operation

Processor and digital circuitry isolated from line voltage

Communications header for network interface

- PROJECT DURATION	: 150 CALENDAR DAYS

Prepared by:								Checked/Reviewed by:

GWYNETH MERIAM G. BORJA					MELINDA T. COLLADO

Supervising Supply Officer						Division Manager A, ASD

Approved by:

CARMELITO FABIAN C. ABITONA

Port Manager, PMO Agusan